## Loads
Case 1 - solar power for DC well pump and a few garage lights only
ELECTRICAL LOAD PROFILE
DC Well Pump, Garage Lights
|  | Watts | Surge | Hrs/day | KwH/month | wH/day | Months | KhW/yr
Watts
DC loads
garage lights |  | 28 | 28 | 0.25 | 0.21292 | 7 | 12 | 2.555
(2 compact fluorescents @ 14w)
well - 12v @ 2.9a |  | 35 | 35 | 0.2 | 0.21292 | 7 | 12 | 2.555
Running
| Watts | 63 | 63 |  | wH/day = | 14 |  | 5.11

## Battery Sizing
BATTERY SIZING CALCULATION WORKSHEET
DC Well Pump, Garage Lights
Sizing Parameters Chosen:
System Voltage |  | 12 | v |  |  | Max DOD |  | 0.7
Inverter Efficiency |  | 100 | % (none needed) |  |  | Nom. SOC |  | 0.9
Days Autonomy |  | 4 |  |  |  | Low Temp |  | 0.7
[6 empty] | AH per | [7 empty] | Low
WH |  | System |  | Inverter |  | Day |  | Days of |  | Max |  | Nom. |  | Temp |  | Total AH
Required | / | Voltage | / | Efficiency | = | Needed | X | Autonomy | / | DOD | / | SOC | / | Corr. | = | Needed
14 |  | 12 |  | 1 |  | 1.1667 |  | 4 |  | 0.75 |  | 0.9 |  | 0.7 |  | 9.8765
System |  | Battery |  | Batteries
Voltage | / | Voltage | = | in Series
12 |  | 6 |  | 2
Total AH |  | Battery |  | Batteries |  |  |  | Total
Required | / | Rated AH | = | in Parallel |  |  |  | Batteries
9.8765 |  | 225 |  | 1 |  |  |  | Needed: | 2
Selected
Battery: |  | Trojan T105
Type |  | Lead-Acid
Voltage |  | 6
Rated AH |  | 225
Cost |  | 105

## Array Sizing
ARRAY SIZING CALCULATION WORKSHEET
DC Well Pump, Garage Lights
Sizing Parameters Chosen:
Battery Efficiency |  | 80 | % |  |  | Controller & |  |  |  | Peak Sun
High Module | [5 empty] | Wiring Losses |  | 0.9 |  | Hours |  | 3
Operating Temp |  | 0.93 |  |  |  | Weather |  |  |  | System
Dirt & Dust |  | 0.96 |  |  |  | Conditions |  | 0.97 |  | Voltage |  | 12
AH Needed |  | Battery |  | High Mod |  | Dirt & |  | Wiring |  | Weather |  | Array AH
by Batteries | / | Efficiency | / | Op. Temp | / | Dust | / | Loss | / | Conditions | / | Needed
1.1667 |  | 0.8 |  | 0.93 |  | 0.96 |  | 0.9 |  | 0.97 |  | 1.8711
Array AH |  | Peak Sun |  | Array Amps |  | Module |  | Modules in
Needed | / | Hours | = | Needed | / | Amps | = | Parallel
1.8711 |  | 3 |  | 0.62369 |  | 3.56 |  | 1
System |  | Module |  | Modules in |  |  |  | Total
Voltage | / | Voltage | = | Series |  |  |  | Modules
12 |  | 12 |  | 1 |  |  |  | Needed: | 1
PV Module Information
Make/Model: |  | BP SX60U
Nominal Volts |  | 12
Width " |  | 25
Length " |  | 48
Voltage (V): |  | At STC |  | Open Circuit |  | At High Temp
|  | 16.8 |  | 21 |  | 14.4
Current (A): |  | At STC |  | Short Circuit
|  | 3.56 |  | 3.87
Bypass Diodes |  | yes
Cost |  | 0

## Inverter Sizing
CONTROLLER & INVERTER CALCULATIONS WORKSHEET
DC Well Pump, Garage Lights
Charge Controller Requirements
|  | Module Short | X | Modules in |  | Array Short
System Voltage (V) |  | Circuit Current | 1.25 | X Parallel | = | Circuit Amps
12 |  | 3.87 | 4.8375 | 1 |  | 4.8375
DC Total |  | DC System |  | Max DC
Connected Watts | / | Voltage | = | Load Amps
63 |  | 12 |  | 5.25
Features needed: |  | Low Voltage
|  | Disconnect? | yes
|  | Marine Envr? | no
Metering
|  | LED's? | yes
|  | UL Listed | yes
Controller Selected:
Make/Model: |  | Xantrex C12 |  | Temp Compensation |  | yes
Rated Voltage (V) |  | 12 |  | LVD |  | yes
PV Current Rating (A) |  | 12 |  | Metering LED's |  | yes
DC Load Amps |  | 12 |  | UL Listed |  | yes
Cost |  | 110
Inverter Requirements (none)

## Wire Sizing
SYSTEM WIRE SIZING WORKSHEET
DC Well Pump, Garage Lights
PV Combiner Box to Controller to Battery:
NEC Calculation
[6 empty] | NEC |  | Amperage
Module Short |  | NEC |  | Modules in |  | Required |  | Meeting | Wire
Circuit Current | X | Requirement | X | Parallel | = | Amps |  | NEC | Size
3.87 |  | 1.56 |  | 1 |  | 6.0372 |  | 40 | 10
(AWG #12 minimum if under 50v DC)
Voltage Drop
Calculation
[6 empty] | Module |  | Acceptable
System |  | One-Way |  | Total ft |  | Total Amps | Voltage | Voltage | R/1000' | Wire
Voltage |  | Distance (ft) | X | 2 |  | (not x1.56) | Drop % | Drop (V) | needed | Size
12 |  | 20 |  | 40 |  | 3.87 | 5 | 0.6 | 3.876 | 10
|  | Largest Gauge |  |  |  | Wire
|  | Wire from NEC |  |  |  | Type
|  | or Voltage Drop | = | AWG #10 |  | THWN
Battery to Inverter: | (none needed)
DC Branch Circuits:
Acceptable
System |  | One-Way |  |  |  | DC Load | Voltage | Voltage | R/1000' | Wire | Wire
Voltage |  | Distance (ft) | X | 2 = Total Ft |  | Amps | Drop % | Drop (V) | needed | Size | Type
12 |  | 20 |  | 40 |  | 5.25 | 1 | 0.12 | 0.57143 | 12 | NMB

## Materials
MATERIALS AND EXPENSES WORKSHEET
DC Well Pump, Garage Lights
Costs
Description |  | Quantity | Unit | Amount
PV Modules
BP SX60U |  | 1 | 0 | 0
Uni-Rac U-RV/28 mount |  | 1 | 66 | 66
Rack shipping |  | 1 | 14 | 14
Batteries
Trojan T105 |  | 2 | 105 | 210
battery shipping (local) |  | 0 | 30 | 0
Cables AWG 2 |  | 2 | 5 | 10
Charge Controller
Xantrex C12 |  | 1 | 110 | 110
shipping |  | 1 | 8 | 8
THHN #10 |  | 10 | 0.17 | 1.7
Disconnects & Fuses
DC Loads Breaker Box |  | 1 | 50 | 50
20-Amp DC breakers (w/box) |  | 2 | 0 | 0
30-Amp DC fuses |  | 1 | 18 | 18
Lightning Arrestor |  | 1 | 35 | 35
Misc
Ground wire |  | 30 | 0.29 | 8.7
NMB #12 |  | 30 | 0.2 | 6
NM #12 |  | 30 | 0.2 | 6
Misc Hardware |  | 1 | 15 | 15
Conduit fittings & tubes |  | 1 | 30 | 30
Shurflo 9300 pump |  | 1 | 660 | 660
shipping for pump |  | 1 | 12 | 12
Lamps |  | 2 | 25 | 50
========
Total Materials |  |  |  | 1310.4
Sales Tax |  |  |  | 14.742
|  |  | Total = | 1325.142